## Slide 1: Case study: Synthetic heatwave/wildfire
Load increased by 50%
PV reduced by 75%
More extreme than actual Aug2020 event
Total shortfall 8/15/2019 – 8/20/2019
  Before adding event: 3.13 GWh
  After adding event: 32.52 GWh
Original data (daily integrals)
Modified data (daily integrals)

## Slide 2: Capacity needed to cover event
10.4x more initial shortfall
6x larger battery capacity required to eliminate load curtailment
Chart: Curtailed Load vs. Battery Capacity
| 0 | 1 | 2 | 3 | 4 | 8 | 12 | 18 | 21 | 22 | 23 | 24
with event | 40.25 | 31.45 | 25.15 | 21.37 | 19.89 | 15.89 | 11.89 | 5.89 | 2.89 | 1.89 | 0.89 | 0
without event | 10.86 | 5.15 | 1.82 | 0.24 | 0

## Slide 3: Example trace
Q=18GWh
Undersupply runs just over two days
Batter capacity changes the magnitude of the under supply, but not the timing
Renewable shifting / fossil minimization
undersupply
preparation
stressed
Renewable shifting / fossil minimization

## Slide 4: Example trace
Q=23GWh
Undersupply runs just over two days
Batter capacity changes the magnitude of the under supply, but not the timing
Renewable shifting / fossil minimization
undersupply
preparation
stressed
Renewable shifting / fossil minimization

## Slide 5: Example trace
Q=24GWh
Undersupply runs just over two days
Batter capacity changes the magnitude of the under supply, but not the timing
Until the undersupply time is eliminated
Renewable shifting / fossil minimization
preparation
stressed
Renewable shifting / fossil minimization